## Assumptions
Solar Carport Project - Evergreen, CO 80439
SITE CONDITIONS
Address | 27424 Pine Valley Dr, Evergreen, CO 80439
Elevation | 7,500 ft
Ground Snow Load (ASCE 7-10) | 60 PSF
Wind Speed (ASCE 7-10) | 110 MPH (3-sec gust)
Exposure Category | B
Risk Category | II
Extreme Low Temperature | -25°C (-13°F)
Frost Depth | ~36 inches
Soil Type | Rocky decomposed granite
AHJ | Jefferson County
Utility | Xcel Energy
Code Cycle | 2023 NEC
Avg Monthly Usage | 1,600 kWh
Annual Usage | 19,200 kWh
EXISTING SYSTEM
Roof Array | 3.6 kW DC (20x Schüco 180W)
String Inverter | ABB PVI-3.6-OUTD-US
Hybrid Inverter | Magnum MS4024PAE (4 kW, 24V)
Battery | EG4 13 kWh
Coupling | AC-coupled (ABB → Magnum)
Magnum Passthrough | 30A per leg
Roof Annual Production (est) | ~4,600 kWh
PROPOSED CARPORT SYSTEM
Panels | 18x 440W
DC Capacity | 7.92 kW
Microinverters | 18x Enphase IQ8A
Structure | ChikoUSA Maximo 185 (2-car)
Tilt | 5° (fixed)
Azimuth | 180° (south)
Est. Annual Production (5° tilt) | ~10,150 kWh
Est. Annual Production (20° tilt) | ~11,090 kWh
Combined System DC | 11.52 kW
Combined Annual Production | ~14,750 kWh
Net Metering Cap (120%) | 23,040 kWh

## Structural
Structural Analysis - Carport Options
Parameter | ChikoUSA Maximo 185 | MT Solar (Custom) | DPW MPM-G2 | Non-Solar Carport
Tilt Angle | 5° (fixed) | 5-30° (adjustable) | 20° (seasonal adj.) | Flat / low pitch
Wind Rating | 185 MPH | Site-specific (custom) | 115 MPH | 90-120 MPH typical
Snow Load Rating | 60 PSF | Site-specific (custom) | 15 PSF | 30-40 PSF typical
Meets Site Requirements? | YES (60 PSF / 110 MPH) | YES (engineered to site) | NO (15 PSF < 60 PSF) | VARIES - check spec
Material | S350 steel, ZAM coating | Aluminum / steel | Hot-dip galvanized steel | Galvanized steel
Certification | UL 2703 | UL 2703 | UL 2703 | None (solar-specific)
Warranty | 10-yr quality, 25-yr life | Varies, typically 10-20 yr | 10-yr quality | 5-10 yr typical
Panel Capacity (2-car) | 18 panels | 18+ panels | 16-18 panels | N/A
Engineering Included | CA/AZ PE stamp | Full custom PE stamp | Standard PE stamp | Varies by vendor
CO PE Stamp | Need local review ($1.5-3K) | Included in custom price | N/A (doesn't meet loads) | May need for >200 sq ft
Dimensions (2-car) | 22.5' x 22.5' | Custom | ~20' x 20' | 20' x 20' typical
Anchor Bolts Included | NO (24x 1" F1554 needed) | Typically included | Varies | Usually included
Structure Cost | $5,600 | $12,000 - $16,000 | ~$4,500 | $3,000 - $5,000
Freight | $800 - $1,200 | Included typically | ~$600 - $1,000 | $500 - $1,200
Anchor Bolts Cost | $550 - $750 | Included | ~$400 | Included or minimal
Total Structure Cost | $6,950 - $7,550 | $12,000 - $16,000 | N/A - DISQUALIFIED | $3,500 - $6,200
TILT ANGLE ANALYSIS (7.92 kW DC Array)
Parameter | 5° Tilt | 15° Tilt | 20° Tilt
kWh/kW/year | 1280 | 1370 | 1400
Annual Production (kWh) | 10138 | 10850 | 11088
Production vs 5° (%) | Baseline | +7.0% | +9.4%
Annual kWh Gain vs 5° | 0 | 712 | 950
Annual $ Gain vs 5° (flat rate) | $0 | $68 | $90
Rise Over 22.5' Depth | 2.0 ft | 6.0 ft | 8.2 ft
Max Structure Height | ~10 ft | ~14 ft | ~16+ ft
Snow Shedding | Poor - manual clearing | Moderate | Good - mostly self-clearing
Wind Loading (relative) | 1.0x (baseline) | ~1.5x | ~2.0x
Structure Cost Impact | $0 (ChikoUSA) | +$6,000 - $10,000 (MT Solar) | +$6,000 - $10,000 (MT Solar)
Manual Snow Clearing Needed? | Yes, 5-10x/winter | Occasionally | Rarely
FOUNDATION REQUIREMENTS
Parameter | Value | Notes
Number of Footings | 6 | 3 per side, 2-car config
Footing Type | Drilled piers | Required for rocky soil
Min Depth Below Grade | 36" | Below frost line + 6" safety
Recommended Pier Diameter | 18" - 24" | Per ChikoUSA engineering
Anchor Bolts Per Footing | 4 | 1" dia F1554 Gr36, 24" long
Total Anchor Bolts | 24
Concrete Volume (est) | 3 - 5 cu yd | Depends on pier diameter
Ready-Mix Cost | $190/yd | $570 - $950 total
Rock Drill Rental | $500 - $800/day | 1-2 day rental
DIY Foundation Total | $1,800 - $2,500 | Rock drill + concrete + rebar
Contractor Foundation | $5,000 - $8,000 | Rock excavation premium

## Electrical
Electrical Design & Interconnection
CONDUIT ROUTING COMPARISON
Parameter | Underground (Trench) | Overhead (Along House)
Route Length | ~80 ft (direct line) | ~85-95 ft (follows perimeter)
Conductor | 3x #6 AWG THWN-2 Cu + #10 EGC | 3x #6 AWG THWN-2 Cu + #10 EGC
Conduit Type | 1-1/4" Schedule 80 PVC | 3/4" or 1" EMT or RMC
Burial Depth | 18" min (NEC 300.5), 24" recommended | N/A
Voltage Drop | 1.6% @ 27.5A | 1.7-1.9% @ 27.5A
Voltage Drop Limit | 3% | 3%
Within Limit? | YES | YES
Materials Cost | $850 | $600 - $900
Trenching (DIY) | $300 - $600 (rock saw rental) | N/A
Trenching (Contractor) | $1,500 - $3,000 | N/A
Total Cost (DIY) | $1,150 - $1,450 | $600 - $900
Total Cost (Contractor) | $2,350 - $3,850 | $600 - $900
Visibility | Invisible | Visible on SW exterior
Longevity | 25+ years, protected | 15-25 years (UV/altitude)
Modifiability | Difficult | Easy
Recommended? | YES (if excavating for footings) | Budget fallback
INTERCONNECTION ARCHITECTURE OPTIONS
Parameter | A: Line-Side Tap | B: Load-Side (Magnum) | C: Hybrid + IQ Controller | D: Upgrade Magnum
Grid-Tied Operation | Clean, independent | Works but fragile | Clean, independent | Clean, integrated
Off-Grid (Carport) | DEAD - micros shut down | Can charge battery | Sunlight Backup mode | Full integration
Passthrough Conflict | None (bypasses Magnum) | YES - 42.5A > 30A limit | None | None (solved)
Trip Risk | None | Moderate (cool sunny days) | None | None
Additional Equipment | Fused disconnect only | None | IQ System Controller 3 | Second Magnum or Sol-Ark
Additional Cost | $0 - $200 | $0 | $1,500 - $2,000 | $2,500 - $6,000
Complexity | Low | High risk | Medium | Medium-High
Inspector-Friendly | Very | Questionable | Good | Good
Future Upgradeable | Add IQ Controller later | Stuck with limitation | Already upgraded | Fully capable
RECOMMENDATION | ★ BEST VALUE | NOT RECOMMENDED | GOOD IF RESILIENCE NEEDED | OVERKILL FOR NOW
MAGNUM PASSTHROUGH CALCULATION
Magnum MS4024PAE Passthrough Rating | 30A per leg
Carport Array (7.92 kW @ 240V) | 27.5A continuous
Roof Array (3.6 kW @ 240V) | ~15A continuous
Combined Peak Current | ~42.5A
Overage vs 30A Limit | 12.5A (42%)
Result | EXCEEDS LIMIT - will trip/current-limit

## Economics
Economic Analysis - Solar Carport vs Non-Solar Carport
KEY ASSUMPTIONS
Federal ITC (Section 25D) | EXPIRED 12/31/2025 | Per 'One Big Beautiful Bill'
State/Local Incentives | None identified
Labor Cost Assumption | $0 (owner DIY - JE license)
Electricity Rate Escalation | 3.5% / year | Xcel filed 9.9% for Aug 2026
Panel Degradation | 0.5% / year
Discount Rate (nominal) | 5%
XCEL ENERGY TOU RATES (eff. 11/1/2025)
Period | On-Peak (5-9 PM wkdays) | Off-Peak (all other) | Multiplier
Summer (Jun-Sep) | $0.213/kWh | $0.079/kWh | 2.7x
Winter (Oct-May) | $0.183/kWh | $0.068/kWh | 2.7x
Flat Rate Alternative | $0.100/kWh (summer) | $0.090/kWh (winter) | 1.0x
COST COMPARISON: SOLAR CARPORT vs NON-SOLAR CARPORT
Line Item | Solar Carport (ChikoUSA) | Non-Solar Carport | Solar Premium
Structure | 7250 | 4500 | 2750
Freight / Delivery | 1000 | 800 | 200
Anchor Bolts / Hardware | 650 | 0 | 650
Foundation (DIY drilled piers) | 2150 | 2150 | 0
PE Engineering (CO stamp) | 2250 | 500 | 1750
Panels (18x 440W @ pallet pricing) | 1800 | 0 | 1800
Microinverters (18x IQ8A + combiner + gateway) | 3450 | 0 | 3450
Wire, Conduit, Electrical | 750 | 0 | 750
Trenching / Conduit Routing (DIY) | 400 | 0 | 400
Permits (electrical + building) | 600 | 300 | 300
Miscellaneous | 250 | 100 | 150
TOTAL PROJECT COST | 20550 | 8350 | 12200
ANNUAL SOLAR VALUE
Component | TOU Rate Plan | Flat Rate Plan | Notes
Carport Production (kWh/yr) | 10150 | 10150 | 5° tilt, south-facing
Off-Peak Solar Value | 585 |  | 80% of production @ ~$0.072 avg
On-Peak Solar Value (5-9 PM) | 101 |  | 5% of production @ ~$0.198 avg
Overnight/Morning Value | 109 |  | 15% of production @ ~$0.072 avg
Flat Rate Solar Value |  | 964 | 100% @ ~$0.095 avg
Total Direct Solar Value | 795 | 964
Battery Arbitrage Uplift (from solar) | 200 | 0 | Incremental from carport charging
TOTAL ANNUAL SOLAR VALUE | 995 | 964
PAYBACK ANALYSIS
Scenario | Total Cost | Annual Value | Simple Payback
Solar Carport (full cost, TOU) | 20550 | 995 | 20.6533
Solar Carport (full cost, flat) | 20550 | 964 | 21.3174
Solar Premium Only (TOU) | 12200 | 995 | 12.2613
Solar Premium Only (flat) | 12200 | 964 | 12.6556
Solar Premium + TOU optimization | 12200 | 1495 | 8.1605
★ If building a carport anyway, solar premium payback drops from 20+ years to 8-12 years
BATTERY ARBITRAGE VALUE (Independent of Carport)
EG4 Battery Usable Capacity | 12 kWh (90% DoD of 13 kWh)
Magnum Continuous Discharge | ~3 kW
On-Peak Window | 4 hours (5-9 PM weekdays)
Daily Arbitrage Volume | ~12 kWh
Summer Spread (On - Off) | $0.134/kWh
Summer Daily Value | $1.61
Summer Days | ~122
Summer Arbitrage Value | $196
Winter Spread (On - Off) | $0.115/kWh
Winter Daily Value | $1.38
Winter Days | ~243
Winter Arbitrage Value | $335
ANNUAL BATTERY ARBITRAGE | $531
TOU vs FLAT RATE - HOUSEHOLD ANALYSIS (1,600 kWh/mo)
Load Management Level | % On-Peak | Monthly TOU Cost | Monthly Flat Cost
No management | 30% | $162 - $178 | $152 - $160
Moderate shifting (EV after 9 PM, pre-heat) | 20% | $138 - $152 | $152 - $160
Aggressive + battery arbitrage | 10% | $114 - $126 | $152 - $160
VERDICT: Stay on TOU. With battery + load shifting, save $350-500/yr vs flat rate.
25-YEAR CASH FLOW: SOLAR PREMIUM ANALYSIS (TOU + Optimization)
Assumptions: 3.5% rate escalation, 0.5% panel degradation, $500 inverter replacement yr 15
Year | Solar Value ($) | Cumulative ($) | NPV @ 5% ($)
0 | -12200 | -12200 | -12200
1 | 1540 | -10660 | -10734
2 | 1586 | -9075 | -9296
3 | 1633 | -7442 | -7885
4 | 1681 | -5761 | -6502
5 | 1732 | -4029 | -5145
6 | 1783 | -2246 | -3814
7 | 1836 | -409 | -2509
8 | 1891 | 1482 | -1229
9 | 1948 | 3430 | 26
10 | 2006 | 5435 | 1258
11 | 2066 | 7501 | 2465
12 | 2127 | 9628 | 3650
13 | 2191 | 11819 | 4812
14 | 2256 | 14075 | 5951
15 | 1823 | 15898 | 6828
16 | 2393 | 18290 | 7924
17 | 2464 | 20754 | 8999
18 | 2537 | 23292 | 10053
19 | 2613 | 25905 | 11088
20 | 2691 | 28596 | 12102
21 | 2771 | 31367 | 13096
22 | 2854 | 34221 | 14072
23 | 2939 | 37160 | 15029
24 | 3027 | 40187 | 15967
25 | 3117 | 43303 | 16888
Cumulative turns positive = payback year. NPV positive = project creates real value.

## Equipment
Equipment Sourcing & Pricing
Item | New Price | Used/Discount Price | Recommendation
18x 440W Panels (pallet) | $1,600 - $2,000 | $0.15/W for 300W (worse $/kW) | BUY NEW - warranty + efficiency worth $554 diff
18x IQ8A Microinverters | $2,700 - $3,240 | $1,440 - $2,160 (used IQ7+) | BUY NEW - 25yr warranty, remote location risk
IQ Combiner 4 + Gateway | $500 - $700 | Rarely available used | BUY NEW
ChikoUSA Maximo 185 | $5,600 | N/A (no secondary market) | Only option meeting loads
Anchor Bolts (24x F1554) | $550 - $750 | $200 (FB Marketplace cut-downs) | Check FB/Craigslist first
Wire (3x #6 THWN-2 Cu) | $400 - $600 | $350 - $500 (surplus) | Check Mile High Surplus, ReStore
Conduit (Sch 80 PVC / EMT) | $200 - $350 | $150 - $250 (surplus) | Check surplus stores
Foundation Materials | $950 - $1,500 | N/A (concrete is concrete) | Ready-mix at $190/yd

## Action Items
Action Items & Decision Framework
IMMEDIATE ACTIONS (No Capital Required)
# | Action | Est. Savings | Cost | Notes
1 | Install timer on EV charging circuit (after 9 PM only) | $100-200/yr | $30-50 | Immediate ROI
2 | Program Magnum for daily battery arbitrage | $530/yr | $0 | Charge day, discharge 5-9 PM
3 | Pre-heat hot tub before 5 PM, coast through peak | $50-100/yr | $0 | Timer or smart plug
4 | Thermostat pre-conditioning before 5 PM | $50-100/yr | $0 | Smart thermostat schedule
5 | TOTAL IMMEDIATE SAVINGS | $350-500/yr | $30-50 | Available TODAY
PRE-CONSTRUCTION ACTIONS (If Proceeding)
# | Action | Timeline | Cost | Contact
1 | Call JeffCo Planning - confirm setbacks/height | Week 1 | $0 | 303-271-8700
2 | Contact ChikoUSA - CO PE stamp availability | Week 1 | $0 | 1-800-948-5390
3 | Get foundation contractor quotes (rock drilling) | Week 2-3 | $0 | Min 2 quotes
4 | Order ChikoUSA Maximo 185 | Week 3-4 | $5,600 | Signature Solar
5 | Order panels at pallet pricing | Week 3-4 | $1,600-2,000 | CED Greentech / Soligent
6 | Order IQ8A micros + combiner + gateway | Week 3-4 | $3,200-3,700 | Enphase distributor
7 | Engage CO PE for site-specific stamp | Week 2-4 | $1,500-3,000
8 | Submit permits (building + electrical) | Week 5-6 | $400-800 | JeffCo