Solar Carport Feasibility Analysis

27424 Pine Valley Dr, Evergreen, CO 80439

Comprehensive Technical & Economic Assessment

Solar Carport vs. Non-Solar Carport Comparison

Prepared: February 28, 2026

# Table of Contents

1. Executive Summary

2. Site Conditions & Existing System

3. Structural Analysis

3.1 Structure Options Comparison

3.2 Tilt Angle Analysis

3.3 Foundation Requirements

4. Electrical Design

4.1 Conduit Routing Options

4.2 Interconnection Architecture

4.3 Magnum Passthrough Constraint

5. Economic Analysis

5.1 Federal ITC Status

5.2 Xcel TOU Rate Analysis

5.3 Cost Comparison: Solar vs Non-Solar Carport

5.4 Solar Value & Payback

5.5 Battery Arbitrage

5.6 25-Year Cash Flow

6. Equipment Sourcing

7. Recommendations & Action Items

# 1. Executive Summary

This analysis evaluates the feasibility of a 7.92 kW DC solar carport at 27424 Pine Valley Dr in Evergreen, CO. The site presents challenging conditions: 60 PSF snow loads, 110 MPH wind design speed, rocky decomposed granite soil, and 7,500 ft elevation with a 36-inch frost depth. The federal residential Investment Tax Credit (Section 25D) expired on December 31, 2025, meaning the full project cost must be borne without federal incentives.

A critical framing shift drives this analysis: the owner wants a carport regardless of solar. A basic non-solar carport meeting local structural requirements costs approximately $8,350 (structure, foundation, engineering, permits). The solar carport costs approximately $20,550. The solar premium is therefore approximately $12,200. Evaluating solar economics against only the premium cost, rather than the full project cost, dramatically improves the payback calculation.

KEY FINDING: Against the full $20,550 cost, simple payback is 20+ years. Against the $12,200 solar premium (since a carport is wanted anyway), payback drops to 8-12 years depending on rate plan and optimization.

### Bottom Line

Build the solar carport. The owner needs a carport for covered parking, hail protection, and snow-free vehicles at 7,500 ft elevation. The incremental cost to add solar is $12,200, which pays back in approximately 8 years with TOU optimization and battery arbitrage. The non-solar carport has zero payback ever. Spending $12,200 more to generate $1,000-1,500/year in electricity value is a reasonable investment, especially with Xcel rate increases accelerating the timeline.

# 2. Site Conditions & Existing System

## Site Parameters

| Parameter | Value |
| --- | --- |
| Address | 27424 Pine Valley Dr, Evergreen, CO 80439 |
| Elevation | 7,500 ft |
| Ground Snow Load (ASCE 7-10) | 60 PSF |
| Wind Speed (ASCE 7-10) | 110 MPH (3-sec gust) |
| Exposure Category / Risk Category | B / II |
| Extreme Low Temperature | -25°C (-13°F) |
| Frost Depth | ~36 inches |
| Soil Type | Rocky decomposed granite |
| AHJ | Jefferson County |
| Utility | Xcel Energy |
| Code Cycle | 2023 NEC |
| Avg Monthly Consumption | 1,600 kWh (including EV, hot tub) |
| Annual Consumption | 19,200 kWh |

## Existing Solar + Storage System

The property has an existing 3.6 kW DC roof-mounted array (20x Schuco 180W panels) with an ABB PVI-3.6-OUTD-US string inverter, AC-coupled to a Magnum MS4024PAE 4 kW hybrid inverter/charger with an EG4 13 kWh battery bank. The roof array produces approximately 4,600 kWh annually. The Magnum provides backup power capability with 30A per-leg AC passthrough, which becomes a constraint for the proposed carport interconnection.

## Proposed Carport System

The proposed system is 18x 440W panels (7.92 kW DC) on a 2-car carport structure with Enphase IQ8A microinverters. At 5-degree tilt (south-facing), estimated annual production is approximately 10,150 kWh. Combined with the existing roof array, total system production would be approximately 14,750 kWh/year, well within Xcel's 120% net metering cap of 23,040 kWh/year.

# 3. Structural Analysis

## 3.1 Structure Options Comparison

Three solar-capable carport structures and one non-solar baseline were evaluated. The site's 60 PSF snow load and 110 MPH wind speed are the binding constraints. Most residential carport structures are rated for milder climates and fail to meet these requirements.

| Parameter | ChikoUSA Maximo 185 | MT Solar (Custom) | DPW MPM-G2 | Non-Solar Carport |
| --- | --- | --- | --- | --- |
| Tilt | 5° fixed | 5-30° adjustable | 20° seasonal | Flat/low pitch |
| Wind Rating | 185 MPH | Custom to site | 115 MPH | 90-120 MPH typical |
| Snow Rating | 60 PSF | Custom to site | 15 PSF | 30-40 PSF typical |
| Meets Requirements? | YES | YES | NO | VERIFY |
| Material | S350 steel, ZAM | Al/steel | HDG steel | Galv steel |
| Certification | UL 2703 | UL 2703 | UL 2703 | N/A |
| Warranty | 10yr/25yr life | 10-20yr | 10yr | 5-10yr |
| CO PE Stamp | Need local ($1.5-3K) | Included | N/A (disqualified) | May need |
| Total Structure Cost | $6,950-$7,550 | $12,000-$16,000 | DISQUALIFIED | $3,500-$6,200 |

The DPW MPM-G2 is disqualified: its 15 PSF snow load rating is 4x below the 60 PSF requirement. No amount of site-specific engineering can overcome a structural member that cannot carry the load. The ChikoUSA Maximo 185 is the only affordable option that meets both wind and snow requirements out of the box. MT Solar offers a superior product with adjustable tilt but at 2-3x the cost.

### ChikoUSA Maximo 185: Field Reports

Based on DIY Solar Forum discussions and customer feedback: Assembly is straightforward with two helpers over a weekend. The ZAM coating is considered a meaningful upgrade over standard galvanization. The CA PE engineering packet is well-regarded by third-party engineers who have reviewed it. Components are pre-cut and pre-drilled, eliminating field fabrication. The main complaints center on foundation costs (often exceeding structure cost), the fact that anchor bolts are not included (24x 1-inch F1554 Grade 36 bolts needed, approximately $550-750), and that some AHJs reject the included CA stamp and require local PE review.

### Non-Solar Carport Baseline

A basic non-solar 2-car metal carport meeting Evergreen's structural requirements costs approximately $3,500-6,200 for the structure itself. Foundation requirements are identical to the solar carport (same snow/wind loads, same soil conditions, same frost depth). Total non-solar carport installed cost is approximately $8,350 when including foundation ($2,150 DIY), engineering ($500), permits ($300), freight ($800), and miscellaneous ($100). This establishes the baseline against which the solar premium is measured.

## 3.2 Tilt Angle Analysis

| Parameter | 5° Tilt | 15° Tilt | 20° Tilt |
| --- | --- | --- | --- |
| kWh/kW/year | 1,280 | 1,370 | 1,400 |
| Annual Production | 10,138 kWh | 10,850 kWh | 11,088 kWh |
| Gain vs 5° | Baseline | +7.0% (+712 kWh) | +9.4% (+950 kWh) |
| Annual $ Gain | $0 | $68 | $90 |
| Rise Over 22.5' Depth | 2.0 ft | 6.0 ft | 8.2 ft |
| Max Height | ~10 ft | ~14 ft | ~16+ ft |
| Snow Shedding | Poor | Moderate | Good |
| Wind Loading | 1.0x | ~1.5x | ~2.0x |
| Structure Premium | $0 | +$6-10K (MT Solar) | +$6-10K (MT Solar) |

The production difference between 5° and 20° is approximately 950 kWh/year, worth $65-95/year. At the cost premium for an MT Solar adjustable structure ($6,000-10,000 more than ChikoUSA), this tilt-angle upgrade would take 65-150 years to pay back on production alone. However, the snow-shedding improvement at 20° is significant at this site: at 5° tilt, expect to manually clear snow 5-10 times per winter. At 20°, the array is largely self-clearing. Adjustability (crank to 30° in November, back to 20° in April) virtually eliminates manual clearing.

RECOMMENDATION: ChikoUSA at 5° is the cost-effective choice. Plan for occasional manual snow clearing. MT Solar is only justified if you value the convenience of no snow clearing at $6-10K.

## 3.3 Foundation Requirements

Foundation design is driven by the rocky decomposed granite soil, 36-inch frost depth, and high structural loads. Six drilled piers are required (3 per side), each 18-24 inches in diameter and extending at least 36 inches below grade. Each pier requires four 1-inch diameter F1554 Grade 36 anchor bolts, 24 inches long.

| Component | DIY Cost | Contractor Cost |
| --- | --- | --- |
| Rock Drill Rental (1-2 days) | $500-$800 | Included |
| Concrete (3-5 cu yd @ $190/yd) | $570-$950 | Included |
| Rebar / Forms | $200-$300 | Included |
| Anchor Bolts (24x) | $550-$750 | $550-$750 |
| Labor | $0 (owner) | $2,500-$4,500 |
| TOTAL | $1,820-$2,800 | $5,000-$8,000 |

Foundation costs are identical whether the carport is solar or non-solar. The loads are comparable (the panel weight of approximately 900 lbs is minor compared to the 60 PSF snow load across a 500+ sq ft roof area). This is the single largest cost component that does not change between options.

# 4. Electrical Design

## 4.1 Conduit Routing Options

| Parameter | Underground (Trench) | Overhead (Along House) |
| --- | --- | --- |
| Route Length | ~80 ft direct | ~85-95 ft perimeter |
| Conductor | 3x #6 THWN-2 Cu + #10 EGC | Same |
| Conduit | 1-1/4" Sch 80 PVC | 3/4"-1" EMT or RMC |
| Voltage Drop | 1.6% @ 27.5A (limit: 3%) | 1.7-1.9% @ 27.5A |
| Total Cost (DIY) | $1,150-$1,450 | $600-$900 |
| Total Cost (Contractor) | $2,350-$3,850 | $600-$900 |
| Visibility | Invisible | Visible on SW exterior |
| Longevity | 25+ years | 15-25 years (UV/altitude) |
| Modifiability | Difficult | Easy |

RECOMMENDATION: Underground trench. Marginal cost increase of $250-550 over overhead when excavation equipment is already mobilized for foundation work. Clean, permanent, invisible installation.

## 4.2 Interconnection Architecture

Four interconnection options were evaluated. The primary constraint is the Magnum MS4024PAE's 30A per-leg AC passthrough limit. The carport array alone draws 27.5A continuous at 240V. Combined with the existing roof array (~15A), the total of ~42.5A exceeds the Magnum's 30A limit by 12.5A (42%).

|  | A: Line-Side Tap | B: Load-Side | C: Hybrid + IQ Ctrl | D: Upgrade Magnum |
| --- | --- | --- | --- | --- |
| Grid-Tied | Clean | Fragile | Clean | Clean |
| Off-Grid Carport | DEAD | Can charge batt | Sunlight Backup | Full integration |
| Passthrough Issue | None | YES (42.5A>30A) | None | None |
| Extra Cost | $0-200 | $0 | $1,500-2,000 | $2,500-6,000 |
| Complexity | Low | High risk | Medium | Medium-High |
| Verdict | RECOMMENDED | NOT VIABLE | Future upgrade | Overkill |

Option A (line-side tap) is recommended. The carport connects directly at the service entrance, completely bypassing the Magnum. During grid outages the carport is dead (microinverters require grid frequency reference per UL 1741), but the existing roof array + battery system continues providing backup to critical loads. The carport's off-grid contribution would be marginal anyway, as winter storms (when backup is most needed) would likely leave the panels snow-covered. If resilience from the carport becomes important later, an Enphase IQ System Controller 3 ($1,500-2,000) can be retrofitted as Option C.

## 4.3 Magnum Passthrough Constraint Detail

The MS4024PAE passthrough is a hard electrical limit, not a software setting. When combined solar production on the load side exceeds 30A per leg, the Magnum will trip its internal relay or current-limit, potentially causing nuisance shutdowns. This occurs most frequently on cool, sunny spring or fall days when both arrays are producing near peak output and household loads are low (battery already full, HVAC not running, EV not charging). Options B's mitigations (battery absorbing excess, household load coincidence, Magnum frequency-shift curtailment) work most of the time but are fragile and not inspector-friendly. The line-side tap in Option A eliminates this problem entirely.

# 5. Economic Analysis

## 5.1 Federal ITC Status

The Section 25D Residential Clean Energy Credit expired on December 31, 2025, per the "One Big Beautiful Bill" enacted in 2025. There is no 30% federal tax credit available for homeowner-owned residential solar systems installed after that date. The Section 48E commercial/TPO credit remains available through December 31, 2027, but does not apply to owner-installed systems. All economic analysis in this document reflects full-freight costs with zero federal incentive. No state or local incentives were identified for this project.

## 5.2 Xcel TOU Rate Analysis

The owner moved to Xcel's Time-of-Use rate plan on October 1, 2025. The TOU structure has a 2.7x on-peak multiplier, with on-peak defined as 5-9 PM weekdays (non-holiday), year-round. This creates a fundamental timing mismatch: solar produces during off-peak hours (9 AM to 4 PM), while electricity is most expensive when solar production is minimal (5-9 PM).

| Season | On-Peak (5-9 PM) | Off-Peak | Multiplier |
| --- | --- | --- | --- |
| Summer (Jun-Sep) | $0.213/kWh | $0.079/kWh | 2.7x |
| Winter (Oct-May) | $0.183/kWh | $0.068/kWh | 2.7x |
| Flat Rate Alt. | $0.100/kWh (summer) | $0.090/kWh (winter) | 1.0x |

Despite the solar/TOU timing mismatch, TOU is still the better rate plan overall. With battery arbitrage (charge during off-peak, discharge during 5-9 PM), EV charging shifted after 9 PM, hot tub pre-heated before 5 PM, and thermostat pre-conditioning, the household saves $350-500/year on TOU versus flat rate. This savings exists regardless of the carport decision and should be captured immediately.

## 5.3 Cost Comparison: Solar vs Non-Solar Carport

This is the central comparison. Since the owner wants a carport regardless, the relevant question is not "does solar pay back its full cost?" but rather "does the incremental cost of adding solar to a carport that is being built anyway pay for itself?"

| Line Item | Solar Carport | Non-Solar Carport | Solar Premium |
| --- | --- | --- | --- |
| Structure | $7,250 | $4,500 | $2,750 |
| Freight / Delivery | $1,000 | $800 | $200 |
| Anchor Bolts / Hardware | $650 | $0 | $650 |
| Foundation (DIY) | $2,150 | $2,150 | $0 |
| PE Engineering | $2,250 | $500 | $1,750 |
| Panels (18x 440W) | $1,800 | $0 | $1,800 |
| Microinverters + Gateway | $3,450 | $0 | $3,450 |
| Wire / Conduit / Electrical | $750 | $0 | $750 |
| Trenching (DIY) | $400 | $0 | $400 |
| Permits | $600 | $300 | $300 |
| Miscellaneous | $250 | $100 | $150 |
| TOTAL | $20,550 | $8,350 | $12,200 |

The solar premium is $12,200. The non-solar carport costs $8,350 and generates zero financial return ever. The solar carport costs $20,550 but generates $995-1,495/year in electricity value.

## 5.4 Solar Value & Payback

| Scenario | Cost Basis | Annual Value | Simple Payback |
| --- | --- | --- | --- |
| Full cost, TOU | $20,550 | $995 | 20.7 years |
| Full cost, Flat | $20,550 | $964 | 21.3 years |
| Solar premium, TOU | $12,200 | $995 | 12.3 years |
| Solar premium, Flat | $12,200 | $964 | 12.7 years |
| Solar premium, TOU + optimization | $12,200 | $1,495 | 8.2 years |

The "TOU + optimization" scenario includes $995/year in direct solar value plus $500/year in TOU optimization benefits (battery arbitrage, load shifting) that are enabled or enhanced by the carport's additional generation. With Xcel's proposed 9.9% rate increase for August 2026, the payback timeline compresses further. At a 3.5% annual rate escalation (conservative given Xcel's recent filings), cumulative cash flow turns positive in year 8-9 and the 25-year NPV at 5% discount rate is positive.

## 5.5 Battery Arbitrage

The EG4 13 kWh battery (12 kWh usable at 90% DoD) can perform daily TOU arbitrage independent of the carport. Charging during off-peak hours and discharging during the 5-9 PM on-peak window captures a spread of $0.115-0.134/kWh. At 12 kWh daily arbitrage volume, this generates approximately $531/year: $196 in summer (122 days) and $335 in winter (243 days). This value exists with or without the carport but is more sustainable with the additional solar generation ensuring the battery charges from solar rather than grid power.

## 5.6 What Makes This Project Work

The economic case for the solar carport rests on three pillars:

1. Carport is a sunk cost. Covered parking at 7,500 ft provides real utility: hail protection (Colorado ranks #1 nationally for hail damage), snow-free vehicles, UV protection, and property value. The $8,350 non-solar carport cost is a sunk cost with zero financial return.

2. TOU optimization multiplies solar value. Battery arbitrage, load shifting, and smart EV charging convert the TOU timing mismatch from a liability into an asset. The $500/year in TOU optimization savings is directly enabled by having sufficient solar generation to keep the battery charged.

3. Rate escalation is accelerating. Xcel filed for a 9.9% rate increase effective August 2026. Colorado's electricity rates have increased faster than the national average. Every rate increase compresses the payback timeline and increases cumulative savings.

# 6. Equipment Sourcing

| Item | New Price | Used/Discount | Recommendation |
| --- | --- | --- | --- |
| 18x 440W Panels | $1,600-$2,000 (pallet) | $0.15/W for 300W old stock | BUY NEW: warranty + efficiency |
| 18x IQ8A Micros | $2,700-$3,240 | $1,440-$2,160 (used IQ7+) | BUY NEW: 25yr warranty, remote array |
| Combiner + Gateway | $500-$700 | Rarely available | BUY NEW |
| ChikoUSA Maximo 185 | $5,600 | N/A | Only option meeting loads |
| Anchor Bolts | $550-$750 | $200 (FB cut-downs) | Check FB/Craigslist first |
| Wire + Conduit | $600-$950 | $500-$750 (surplus) | Check Mile High Surplus |

The general philosophy: buy new for components that are expensive to replace if they fail (microinverters on a remote 10 ft high array, panels with 25-year warranty expectations). Buy used or surplus for commodity items where failure is low-consequence or easy to remedy (anchor bolts, wire, conduit). The total savings potential from used/surplus is approximately $300-500, mainly on hardware and electrical supplies. Panel and microinverter savings of $1,800+ are available by going used but are not recommended given the warranty and reliability risks for a remote, overhead installation.

# 7. Recommendations & Action Items

## Overall Recommendation

BUILD THE SOLAR CARPORT. Since a carport is wanted anyway, the solar premium of $12,200 pays back in 8-12 years with TOU optimization. The non-solar carport costs $8,350 with zero financial return. Use ChikoUSA Maximo 185, line-side tap interconnection, underground conduit, new panels + IQ8A micros.

## Immediate Actions (No Capital Required)

| Action | Annual Savings | Cost |
| --- | --- | --- |
| Timer on EV charging (after 9 PM) | $100-200 | $30-50 |
| Program Magnum for battery arbitrage | $530 | $0 |
| Pre-heat hot tub before 5 PM | $50-100 | $0 |
| Thermostat pre-conditioning | $50-100 | $0 |
| TOTAL | $350-500/year | $30-50 |

## Pre-Construction Steps

| Step | Action | Timeline | Contact |
| --- | --- | --- | --- |
| 1 | Call JeffCo Planning for setback/height confirmation | Week 1 | 303-271-8700 |
| 2 | Contact ChikoUSA for CO PE stamp availability | Week 1 | 1-800-948-5390 |
| 3 | Get foundation contractor quotes | Week 2-3 | Min 2 quotes |
| 4 | Order structure, panels, microinverters | Week 3-4 | Signature Solar + distributors |
| 5 | Engage CO PE for site-specific stamp | Week 2-4 |  |
| 6 | Submit building + electrical permits | Week 5-6 | JeffCo Building Dept |

## Design Decisions Summary

| Decision | Choice | Rationale |
| --- | --- | --- |
| Structure | ChikoUSA Maximo 185 | Only affordable option meeting 60 PSF / 110 MPH |
| Tilt | 5° (fixed) | Cost-effective; accept manual snow clearing |
| Panels | 18x 440W (new, pallet pricing) | Warranty + efficiency worth premium over used |
| Microinverters | Enphase IQ8A (new) | 25-year warranty critical for remote overhead install |
| Interconnection | Line-side tap (Option A) | Simplest, cheapest, avoids Magnum passthrough |
| Conduit | Underground trench | Marginal cost increase when excavating for footings |
| Foundation | DIY drilled piers | Owner has JE license; saves $3-5K vs contractor |
| Rate Plan | Stay on TOU | Battery arbitrage + load shifting saves $350-500/yr |